## Heat pump model
Aquatic Centre pool hall |  | This is very rough modelling of pool and pool hall heating only. EnergyPlus includes a detailed pool modelling module
This ignores many aspects and makes lots of assumptions:
replacing energy lost with backwashing water and possible Reverse Osmosis recovery of waste water for reuse
losses from heat distribution system
no heat from lights, equipment or electricity use by lights, appliances, equipment
only looking at pool hall, not rest of centre's activities
Guesstimate of energy overheads from fans, pumps, etc included by reducing net COP of heat pump or efficiency of gas boiler
Pool surface area 600m2 and pool hall area 1200m2
Assumptions to simplify this calculation
energy content of exhaust air = energy content of incoming air + incremental heat if no heat recovery
incremental energy content of exhaust air = sensible heat +latent heat for increase in water vapour content from outdoor temp/humidity to 60% at 30C
building heat loss is additional to potential heat recoverable from exhaust air - ie all space heating sourced from pool heat loss
exhaust air at 30C, 60% humidity unless heat recovery, assumed to return it to ambient conditions
Heat loss to ground is sensitive to water table and soil type: may be much bigger at St Kilda site
[7 empty] | check | 0.4375 | kW/m2 my est of 'typical' per m2 of pool from Duverge
but inc COP
Net electricity for pool hall= |  |  | (1/COP)*(heat loss from pool to pool hall and ground + heat loss from building)
(very simplistic to get ballpark of annual average)
NOTES: backwashing of filters seems to use a lot of water - not clear if this is heated water. If so shifting to use of cold water could save a lot of energy
Heating of pool hall area |  |  |  |  | building | area | Rval | Tdiff | radiation | watts |  | Heat loss to ground may be much higher for St Kilda due to high water table
outputs from sub-models |  |  |  |  | roof | 1200 | 1.5 | 10 |  | 8000 |  | ground heat loss |  |  | 0.37037
Thermal loads kW 20C ambient no sun |  |  | fraction |  | walls gross | 960 | assume length 3 x width of pool hall floor dimensions |  |  |  |  | watts/m2 | 15
bldg | 59.648 |  | 0.11292 |  | glazing % | 30 | [5 empty] | pool area | 786
exhaust air | 466.8 | net impact | 0.88369 |  | glazing area* | 288 | 0.086207 | 10 |  | 33408 |  | tot W | 11790
ground | 11.79 |  | 0.022319 |  | walls net area | 912 | 0.5 | 10 |  | 18240 |  | tot kW | 11.79
other (lights, equipt, people etc) | -10 |  | -0.018931 |  | solar gain/m2 |  |  |  | 500
tot thermal energy required | 528.238 | kW |  |  | glazing % with solar gain |  | 0 | TOT gain | 0 | 0
Assuming no heat recovery | [9 empty] | 59.648 | kW
(* if low-e double glazing, Rval=0.37)
air flow | airchanges/h | 6 |  |  | If single glazed with condensation or air movement Rval=0.086
| pool area | 600
| ceiling ht | 6 |  | LH20/m3 | Exhaust air energy | [5 empty] | air Cp | 0.0012 | MJ/m3-C | (1.2 kg/m3 and 1 kJ/m3 Cp = 1.2 kJ/m3)
| pool hall volume | 7200 | m3 |  |  | Temp | hum% | kJ/m3 |  | Water vapour in air |  | enthalpy H2O | enth H2O+(air from base 0C)
| hall floor area | 1200 | from bldg calc |  | Air in | 20 | 40 | 33 |  | Temp | humidity% | kJ H2O/kg air | kJ/kg air | Tot Cp kJ/m3
[5 empty] | Air out | 30 | 60 | 71.9 |  | 40 | 60 | 75.84 | 42 | 117.84
Heat pump net COP | 8 | (inc pumps fans distribn loss) |  |  | net energyloss/m3 |  |  | 38.9 |  | 40 | 20 | 25.28 | 42 | 67.28
No heat recovery |  |  |  |  | pool hall vol m3 |  |  | 7200 |  | 30 | 60 | 41.88 | 30 | 71.88 | exhaust air
tot kWe | 66.0298 |  |  |  | air changes/hour |  |  | 6 |  | 30 | 40 | 27.92 | 30 | 57.92
assuming thermal energy recoverable=thermal energy added to exhaust air | Net heat required | 61.438 | kW thermal |  | Air vol m3/hr |  |  | 43200 |  | 20 | 40 | 14.972 | 18 | 32.972
if exhaust air energy recovered |  |  |  |  | Air vol/sec |  |  | 12 |  | 10 | 40 | 7.72 | 6 | 13.72
tot kWe | 7.6797 |  |  |  | net energy/sec |  | kW | 466.8 |  | 5 | 40 | 5.44 | 0 | 5.44
if gas 80% eff no heat recovery | 660.2975 | kW gas | 2377.071 | MJ/h gas
[5 empty] | heat loss | 540 | when no cover
Pool heat capacity
length | 50 |  |  | COP | 8
depth | 1.8 |  | HP kWe | kWth | MJ/h | Time to heat 1C
width | 10 |  | 25 | 200 | 720 | 5.25 | hours
vol | 900 | m3 |  |  | for 15C rise | 78.75 | 3.2812 | days
MJ/m3 | 4.2
for 1C change | 3780 | MJ | watts | MJ/h
area | 500 |  | 15 | 0.054
heat loss/m2 | 15 | watts | 7500 | 27
time for 1 C change | 140 | hours

## Heat pump model (2)
Aquatic Centre pool hall |  | This is very rough modelling of pool and pool hall heating only. EnergyPlus includes a detailed pool modelling module
This ignores many aspects and makes lots of assumptions:
replacing energy lost with backwashing water and possible Reverse Osmosis recovery of waste water for reuse
losses from heat distribution system
no heat from lights, equipment or electricity use by lights, appliances, equipment
only looking at pool hall, not rest of centre's activities
Guesstimate of energy overheads from fans, pumps, etc included by reducing net COP of heat pump or efficiency of gas boiler
Pool surface area 600m2 and pool hall area 1200m2
Assumptions to simplify this calculation
energy content of exhaust air = energy content of incoming air + incremental heat if no heat recovery
incremental energy content of exhaust air = sensible heat +latent heat for increase in water vapour content from outdoor temp/humidity to 60% at 30C
building heat loss is additional to potential heat recoverable from exhaust air - ie all space heating sourced from pool heat loss
exhaust air at 30C, 60% humidity unless heat recovery, assumed to return it to ambient conditions
Heat loss to ground is sensitive to water table and soil type: may be much bigger at St Kilda site
[7 empty] | check | 0.4375 | kW/m2 my est of 'typical' per m2 of pool from Duverge
but inc COP
Net electricity for pool hall= |  |  | (1/COP)*(heat loss from pool to pool hall and ground + heat loss from building)
(very simplistic to get ballpark of annual average)
NOTES: backwashing of filters seems to use a lot of water - not clear if this is heated water. If so shifting to use of cold water could save a lot of energy
Heating of pool hall area |  |  |  |  | building | area | Rval | Tdiff | radiation | watts |  | Heat loss to ground may be much higher for St Kilda due to high water table
outputs from sub-models |  |  |  |  | roof | 1200 | 5 | 25 |  | 6000 |  | ground heat loss |  |  | 0.37037
Thermal loads kW 20C ambient no sun |  |  | fraction |  | walls gross | 960 | assume length 3 x width of pool hall floor dimensions |  |  |  |  | watts/m2 | 15
bldg | 59.52 |  | 0.069265 |  | glazing % | 15 | [5 empty] | pool area | 786 | walls and floor
exhaust air | 798 | net impact | 0.92865 |  | glazing area* | 144 | 5 | 25 |  | 720 |  | tot W | 11790
ground | 11.79 |  | 0.01372 |  | walls net area | 1056 | 0.5 | 25 |  | 52800 |  | tot kW | 11.79
other (lights, equipt, people etc) | -10 |  | -0.011637 |  | solar gain/m2 |  |  |  | 500
tot thermal energy required | 859.31 | kW |  |  | glazing % with solar gain |  | 0 | TOT SOL gain | 0 | 0
Assuming no heat recovery | [9 empty] | 59.52 | kW
(* if low-e double glazing, Rval=0.37)
air flow | airchanges/h | 6 |  |  | If single glazed with condensation or air movement Rval=0.086
| pool area | 600
| ceiling ht | 6 |  | LH20/m3 | Exhaust air energy | [5 empty] | air Cp | 0.0012 | MJ/m3-C | (1.2 kg/m3 and 1 kJ/m3 Cp = 1.2 kJ/m3)
| pool hall volume | 7200 | m3 |  |  | Temp | hum% | kJ/m3 |  | Water vapour in air |  | enthalpy H2O | enth H2O+(air from base 0C)
| hall floor area | 1200 | from bldg calc |  | Air in | 5 | 40 | 5.4 |  | Temp | humidity% | kJ H2O/kg air | kJ/kg air | Tot Cp kJ/m3
[5 empty] | Air out | 30 | 60 | 71.9 |  | 40 | 60 | 75.84 | 42 | 117.84
Heat pump net COP | 6 | (inc pumps fans distribn loss) |  |  | net energyloss/m3 |  |  | 66.5 |  | 40 | 20 | 25.28 | 42 | 67.28
No heat recovery |  |  |  |  | pool hall vol m3 |  |  | 7200 |  | 30 | 60 | 41.88 | 30 | 71.88 | exhaust air
tot kWe | 143.2183 |  |  |  | air changes/hour |  |  | 6 |  | 30 | 40 | 27.92 | 30 | 57.92
assuming thermal energy recoverable=thermal energy added to exhaust air | Net heat required | 61.31 | kW thermal |  | Air vol m3/hr |  |  | 43200 |  | 20 | 40 | 14.972 | 18 | 32.972
if exhaust air energy recovered |  |  |  |  | Air vol/sec |  |  | 12 |  | 10 | 40 | 7.72 | 6 | 13.72
tot kWe | 10.2183 |  |  |  | net energy/sec |  | kW | 798 |  | 5 | 40 | 5.44 | 0 | 5.44
if gas 80% eff no heat recovery | 1074.1375 | kW gas | 3866.895 | MJ/h gas
[5 empty] | heat loss | 540 | when no cover
Pool heat capacity
length | 50 |  |  | COP | 8
depth | 1.8 |  | HP kWe | kWth | MJ/h | Time to heat 1C
width | 10 |  | 25 | 200 | 720 | 5.25 | hours
vol | 900 | m3 |  |  | for 15C rise | 78.75 | 3.2812 | days
MJ/m3 | 4.2
for 1C change | 3780 | MJ | watts | MJ/h
area | 500 |  | 15 | 0.054
heat loss/m2 | 15 | watts | 7500 | 27
time for 1 C change | 140 | hours

## Heat pump model (3)
Aquatic Centre pool hall |  | This is very rough modelling of pool and pool hall heating only. EnergyPlus includes a detailed pool modelling module
This ignores many aspects and makes lots of assumptions:
replacing energy lost with backwashing water and possible Reverse Osmosis recovery of waste water for reuse
losses from heat distribution system
no heat from lights, equipment or electricity use by lights, appliances, equipment
only looking at pool hall, not rest of centre's activities
Guesstimate of energy overheads from fans, pumps, etc included by reducing net COP of heat pump or efficiency of gas boiler
Pool surface area 600m2 and pool hall area 1200m2
Assumptions to simplify this calculation
energy content of exhaust air = energy content of incoming air + incremental heat if no heat recovery
incremental energy content of exhaust air = sensible heat +latent heat for increase in water vapour content from outdoor temp/humidity to 60% at 30C
building heat loss is additional to potential heat recoverable from exhaust air - ie all space heating sourced from pool heat loss
exhaust air at 30C, 60% humidity unless heat recovery, assumed to return it to ambient conditions
Heat loss to ground is sensitive to water table and soil type: may be much bigger at St Kilda site
[7 empty] | check | 0.4375 | kW/m2 my est of 'typical' per m2 of pool from Duverge
but inc COP
Net electricity for pool hall= |  |  | (1/COP)*(heat loss from pool to pool hall and ground + heat loss from building)
(very simplistic to get ballpark of annual average)
NOTES: backwashing of filters seems to use a lot of water - not clear if this is heated water. If so shifting to use of cold water could save a lot of energy
Heating of pool hall area | HOT HUMID AIR |  |  |  | building | area | Rval | Tdiff | radiation | watts |  | Heat loss to ground may be much higher for St Kilda due to high water table
outputs from sub-models |  |  |  |  | roof | 1200 | 1.5 | -10 |  | -8000 |  | ground heat loss |  |  | 0.37037
Thermal loads kW 20C ambient no sun |  |  | fraction |  | walls gross | 960 | assume length 3 x width of pool hall floor dimensions |  |  |  |  | watts/m2 | 15
bldg | -102.848 |  | 0.3613 |  | glazing % | 30 | [5 empty] | pool area | 786 | walls and floor
exhaust air | -183.6 | net impact | 0.64498 |  | glazing area* | 288 | 0.086207 | -10 |  | -33408 |  | tot W | 11790
ground | 11.79 |  | -0.041418 |  | walls net area | 912 | 0.5 | -10 |  | -18240 |  | tot kW | 11.79
other (lights, equipt, people etc) | -10 |  | 0.03513 |  | solar gain/m2 |  |  |  | 500
tot thermal energy required | -284.658 | kW |  |  | glazing % with solar gain |  | 30 | TOT sol gain | -43200 | -43200
Assuming no heat recovery | [9 empty] | -102.848 | kW
(* if low-e double glazing, Rval=0.37)
air flow | airchanges/h | 2 |  |  | If single glazed with condensation or air movement Rval=0.086
| pool area | 600
| ceiling ht | 6 |  | LH20/m3 | Exhaust air energy | [5 empty] | air Cp | 0.0012 | MJ/m3-C | (1.2 kg/m3 and 1 kJ/m3 Cp = 1.2 kJ/m3)
| pool hall volume | 7200 | m3 |  |  | Temp | hum% | kJ/m3 |  | Water vapour in air |  | enthalpy H2O | enth H2O+(air from base 0C)
| hall floor area | 1200 | from bldg calc |  | Air in | 40 | 60 | 117.8 |  | Temp | humidity% | kJ H2O/kg air | kJ/kg air | Tot Cp kJ/m3
[5 empty] | Air out | 30 | 60 | 71.9 |  | 40 | 60 | 75.84 | 42 | 117.84
Heat pump net COP | 6 | (inc pumps fans distribn loss) |  |  | net energyloss/m3 |  |  | -45.9 |  | 40 | 20 | 25.28 | 42 | 67.28
No heat recovery |  |  |  |  | pool hall vol m3 |  |  | 7200 |  | 30 | 65 | 45.37 | 30 | 75.37 | exhaust air
tot kWe | -47.443 |  |  |  | air changes/hour |  |  | 2 |  | 30 | 40 | 27.92 | 30 | 57.92
assuming thermal energy recoverable=thermal energy added to exhaust air | Net heat required | -101.058 | kW thermal |  | Air vol m3/hr |  |  | 14400 |  | 20 | 40 | 14.972 | 18 | 32.972
if exhaust air energy recovered |  |  |  |  | Air vol/sec |  |  | 4 |  | 10 | 40 | 7.72 | 6 | 13.72
tot kWe | -16.843 |  |  |  | net energy/sec |  | kW | -183.6 |  | 5 | 40 | 5.44 | 0 | 5.44
if gas 80% eff no heat recovery | -355.8225 | kW gas | -1280.961 | MJ/h gas
[5 empty] | heat loss | 540 | when no cover
Pool heat capacity
length | 50 |  |  | COP | 8
depth | 1.8 |  | HP kWe | kWth | MJ/h | Time to heat 1C
width | 10 |  | 25 | 200 | 720 | 5.25 | hours
vol | 900 | m3 |  |  | for 15C rise | 78.75 | 3.2812 | days
MJ/m3 | 4.2
for 1C change | 3780 | MJ | watts | MJ/h
area | 500 |  | 15 | 0.054
heat loss/m2 | 15 | watts | 7500 | 27
time for 1 C change | 140 | hours